## Slide 1: Distribution / Feeder Automation CHELCO FECA Engineers Conference June 6, 2016 Presented By: Matthew Avery and Mike Kapotsy

## Slide 2: CHELCO Facts
Located in Panhandle of NW Florida
22 Substations (76 Feeders)
System Peak: 241 MW
51,002 Meters (12 meters/mile)
Featured in Touchstone Energy Best Practices
Chart: ASAI
| 2011 | 2012 | 2013 | 2014 | 2015
2011 2012 2013 2014 2015 | 99.986 | 99.983 | 99.988 | 99.98 | 99.985

## Slide 3: CHELCO Reliability
Chart: CAIDI and SAIDI
| 2011 | 2012 | 2013 | 2014 | 2015
CAIDI | 87.904 | 85.707 | 87.586 | 82.343 | 87.404
SAIDI | 72.275 | 90.04 | 63.206 | 105.985 | 77.497
Notes: 2014 year slipped in reliability due to many big storms that were just shy of being classified as MEDs.
Refer back to TSE paper – bad year following article

## Slide 4: Association of Large Distribution Cooperatives (ALDC) - 2014 Reliability
Chart: Reliability: Avg. Minutes per Consumer (Excluding Extreme Storm)
| Brunswick | Carroll | Central AL | Central GA | Central VA | CHELCO | COBB | Connexus | Dakota | DEMCO | EnergyUnited | Farmers | Florida Keys | Greystone | Jackson | LCEC | Middle Tenn | NH Elec | No. Virginia | Ozarks | Pedernales | Rappahannock | SMECO | Snapping Shoals | South Central | Walton
Reliability: Avg. Minutes per Consumer (Excluding Extreme Storm) | 40.858 | 97.03 | 130.13 | 105.9 | 351 | 103.9 | 35.86 | 23.421 | 28.24 | 204 | 79.25 | 129.27 | 55.05 | 159.81 | 62.6 | 74.73 | 160.7 | 425 | 51.33 | 71.4 | 57.7 | 123.8 | 0 | 66.3212 | 330.82 | 74.04

## Slide 5
CHELCO Reliability
Chart: Outages by Cause (2011-2015)
| LIGHTNING/WEATHER | FAILURE FROM TREES | ANIMAL/SQUIRREL | CAUSE UNKNOWN | MATERIAL OR EQUIPMENT FAULT/FAILURE | MAINTENANCE | OTHER | DECAY/AGE OF MATERIAL/EQUIPMENT | MOTOR VEHICLE | OVERLOAD
LIGHTNING/WEATHER FAILURE FROM TREES ANIMAL/SQUIRREL CAUSE UNKNOWN MATERIAL OR EQUIPMENT FAULT/FAILURE MAINTENANCE OTHER DECAY/AGE OF MATERIAL/EQUIPMENT MOTOR VEHICLE OVERLOAD | 25.43 | 20.1 | 18.33 | 11.22 | 8.46 | 7.16 | 4.21 | 2.28 | 1.42 | 1.39
Notes: Pie chart of Types of outages

## Slide 6: Why Feeder Automation?
Current Sectionalizing Plan
2014 Slip in Reliability
Mitigate Storms/Events that do not Qualify as MEDs
Improve Balanced Scorecard in Member Satisfaction and Reliability
Next Logical Step Given Current Sectionalizing Methods
Chart: CHELCO SAIDI
| 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
Actual SAIDI | 200.91 | 143.09 | 152.76 | 131.28 | 130.17 | 132.38 | 145.19 | 83.79 | 72 | 90 | 63 | 106 | 77
*Predicted SAIDI with YFA | 55 | 83 | 63
    *71% of feeders have back-feed capability (54 Feeders)
    *Assuming 50% restoration on feeder level outages
Notes: Current sectionalizing plan is to fuse all taps off the main 3 phase line. OCRs for taps with more than 20 members.
Featured in Touchstone Energy’s Best Practices for Reliability, but given our current sectionalizing across our system, our aggressive ROW clearing, and our general system maintenance.
Members see an outage whether it qualifies as MED or not – automation improves overall reliability which means the member sees less outages – even in MED events
The next logical step is automating the process of an outage.

## Slide 7: Yukon Feeder Automation?
YFA is a server based application that performs Fault Location, Isolation, Service Restoration (FLISR)
YFA restorations typically in the time frame between 30s to 2m depending upon communication system (Radio System ~2 minutes)
Using YFA as a Bolt-On to Existing SCADA
Operators can control YFA through SCADA
Existing Experience with YFA at CHELCO
Notes: Mike Starts

## Slide 8: Yukon Feeder Automation?

## Slide 9: CHELCO Plan
10 Year Implementation (Due to Cost)
Automate 54 Feeders (Out of 76 Feeders Total)
Automating Worst Performing Feeders First
Automate 111 Downline YFA Reclosers (71% of System)
Operations Buy-in
Benefits Expected in Reliability
Total Cost: $3,028,758 (Already Budgeted: $1,528,75)
Cost Per Site:
  YFA Software (One Time Fee) $15,000
  YFA Site License $2,500 (Adjusted as Devices are Added)
  Annual Maintenance Contract 18% (Negotiable)
  Triple Single Recloser/Control $21,500
  SCADA Communications $4,500
Notes: Operations Buy-in: multiple presentations and Q&A with Ops personnel

## Slide 10: Cost Over 10 Years
Chart: 
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
10 Year Implementation | 188350 | 314860 | 259290 | 291260 | 214460 | 236960 | 317610 | 346410 | 403660 | 455897.5
Chart: 
| Software | Hardware (111 Sites) | SCADA Communication
Software Hardware (111 Sites) SCADA Communication | 350757.5 | 2214500 | 463500

## Slide 11: CHELCO Plan
LAUR
PAXT
BAKR
ABRNn

## Slide 12: CHELCO Plan
DFSP
ALAQ
GLEN

## Slide 13: Next Steps
Padmount Switch Gear
Further Sectionalize Line Segments
Analyze Cost of Tying Radial Feeders Together
Notes: Matthew Starts
Next Steps:
Automate padmount switchgear in beach areas,
Add triple single devices in automated sections to further sectionalize.

## Slide 14: Questions?
Matthew Avery, P.E. Vice President of Engineering mavery@chelco.com
850-307-1190
Mike Kapotsy, M.E., P.E. Engineering Services Supervisor mkapotsy@chelco.com
850-307-1198
Levi McNeely Electrical Engineer II lmcneely@chelco.com
850-307-1235